kÖRNYEZETBARÁT

ÁLLÓ KONDENZÁCIÓS KAZÁNOK

Superbox

02

50

70

90

115

125

150

208

210

250

255

290

300

315

350

430

500

Teljesítmény (kW)

530

535

540

640

660

700

710

860

880

1000

1030

1060

1065

1315

1320

1330

1460

1550

1760

2060

2200

2630

2660

2920

3100

50

70

90

115

125

150

208

210

250

255

290

300

315

350

430

500

530

535

540

640

660

700

710

860

880

1000

1030

1060

1065

1315

1320

1330

1460

1550

1760

2060

2200

2630

2660

2920

3100

50

70

90

115

125

150

208

210

250

255

290

300

315

350

430

500

530

535

540

640

660

700

710

860

880

1000

1030

1060

1065

1315

1320

1330

1460

1550

1760

2060

2200

2630

2660

2920

3100

50

Álló kazánok

Zöld: egy égős készülék

Alubox X-treme

70

90

115

125

150

208

210

250

255

290

300

315

350

430

500

Teljesítmény (kW)

530

535

540

640

Kék: iker égős készülék

660

700LX

710

860

880

1000

1030

1060

1065

1315

1320

1330

1460

1550

1760

2060

2200

2630

2660

2920

3100

Alubox

Teljesítmény (kW)

Ultrabox

Teljesítmény (kW)

Álló Kazánok

Alubox X-treme

250-3100 kW teljesítmény tartomány

Aluminum fűtési hőcserélő Alacsony NOx kibocsátás Alacsony füstgázhőmérséklet Modulációs ráta akár 8:100

Hatásfok akár %108,7  EN 15502-1+A1szerint

Alubox

50-2200 kW teljesítmén tartomány Aluminum fűtési hőcserélő Alacsony NOx kibocsátás Alacsony füstgáz hőmérséklet Modulációs ráta akár 14:100

Hatásfok akár %108,2  EN 15502-1+A1szerint

Ultrabox

210-2660 kW teljesítmény tartomány Rozsdamentes acél fűtési hőcserélő Alacsony NOx kibocsátás

Alacsony füstgáz hőmérséklet Modulációs ráta akár 4:100

Hatásfok akár %108,1  EN 15502-1+A1szerint

Superbox

150-1060 kW teljesítmény tartomány Rozsdamentes acél fűtési hőcserélő Alacsony NOx kibocsátás

Alacsony füstgáz hőmérséklet Modulációs ráta akár 3:100

Hatásfok akár %109  EN 15502-1+A1szerint

03

Alubox X-treme

Álló kondenzációs kazán

250-3100 kW teljesítmény tartomány Alacsony NOx kibocsátás

Alacsony füstgáz hőmérséklet Aluminum fűtési hőcserélő Hatásfok akár %108,7 EN 15502-1

+A1szerint

Modulációs ráta 8:100

Kaszkád vezérlés akár 16 kazánig Hermetikus és nem hermetikus füstgáz lehetőségek

Alacsony zajszint Energia Osztály: A

6 bar üzemi nyomás

04

Alubox X-treme

Magas korrózióállósság

Legújabb technológia, alacsony kibocsátású előkeveréses égő Nagy modulációjú és energiahatékony ventilátor

Biztonsági rendszerek:

Fagy védelem

Túlfűtés védelem

Alacsony nyomás és túlnyomás védelem

Füstgáz hőmérséklet és víznyomás védelem

Szivattyú/szelep védelem

Kisebb térfogat,

- Legionella védelem a HMV tartály számára

nagyobb kapacitás.	- Kondenzátum elzáródás védelem szifon

érzékelővel

Ventillátor sebesség védelem

Felületi hőmérséklet védelem

Nagynyomású kapcsoló gázvezetékhez

05

Alubox X-treme

Álló kondenzációs kazán

Műszaki specifikáció

Alubox X-treme

250	 	300	 	350	 	430	 	535	 	640	 	700

| TELJESÍTMÉNY ADATOK | Egység |
| --- | --- |
| Névleges hőterhelés (min/max) | kW | 48,0/242,0 | 48,0/285,0 | 65,0/335,0 | 85,0/425,0 | 102,0/510,0 | 75,0/615,0 | 118,4/672,4 |
| Névleges hőtljesítmény (80/60°C) (min/max | ) | kW | 46,8/237,0 | 46,8/279,5 | 63,7/328,3 | 82,5/416,0 | 99,9/499,8 | 73,8/601,4 | 111,9/650,4 |
| Névleges hőtljesítmény (50/30°C) (min/max) | kW | 51,4/254,0 | 51,4/302,0 | 70,2/351,7 | 91,6/445,9 | 107,1/540,6 | 81,0/641,4 | 127,6/702,0 |
| Fűtési hatásfok (80/60°C) (min/max) | % | 96,0/98,1 | 96,1/98,2 | 96,3/98,0 | 96,8/97,9 | 97,1/98,2 | 97,0/97,9 | 96,4/97,0 |
| Fűtési hatásfok (50/30°C) (min/max) | % | 108,1/105,3 | 107,6/106,2 | 107,1/106,2 | 108,0/105,0 | 107,6/106,1 | 107,5/106,4 | 108,1/104,8 |
| Hatásfok részterhelésnél (36/30°C) | % | 107,6 | 107,5 | 107,5 | 107,6 | 107,4 | 107,6 | 108,8 |
| Modulációs ráta |  | 20:100 | 17:100 | 20:100 | 20:100 | 20:100 | 13:100 | 18:100 |
| HIDRAULIKUS ADATOK |
| Üzemi víznyomás (min/max) | bar | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 |
| Hőcserélő vízmennyisége | lt | 23 | 23 | 36,22 | 43,65 | 51,08 | 58,81 | 81,7 |
| Víz áramlási mennyisége (min/max) | m³/h | 2,2/10,9 | 2,2/12,9 | 3,1/15,2 | 3,9/19,3 | 5,3/23,5 | 3,9/28,4 | 5,5/30,3 |
| Pump head | mWC | 5,9 | 6,6 | 5,4 | 6,0 | 6,2 | 6,2 | 5,9 |
| Max. üzemi hőmérséklet | ˚C | 90 | 90 | 90 | 90 | 90 | 90 | 90 |
| Hőmérséklet korlátozása | ˚C | 95 | 95 | 95 | 95 | 95 | 95 | 95 |
| GÁZ ÉS ÉGÉSTERMÉK ADATOK |
| Gáz típusa |  | G20 | G20 | G20 | G20 | G20 | G20 | G20 |
| Gáz csatlakozási nyomás (G20/G31) | mbar | 20 | 20 | 20 | 20 | 20 | 20 | 20 |
| Füstgáz nyomása | Pa | 60 | 60 | 60 | 71 | 78 | 195 | 220 |
| Égéstermékek áramlási sebessége (min/max | ) g/sn | 22,0/110,0 | 22,0/127,0 | 31/154 | 40/201 | 47/238 | 39/271 | 54/308 |
| CO2 kibocsátás (min/max) | % | 8,92/8,9 | 8,9/9,0 | 9,1/9,2 | 9,2/9,2 | 8,7/8,9 | 8,8/9,1 | 8,9/9,1 |
| Füstgáz hőmérséklet (80/60˚C) (min/max) | ˚C | 56,1/69,2 | 55,8/71,8 | 57,8/68,7 | 59/69 | 57,7/69,5 | 58,1/67,9 | 60,2/73,5 |
| Füstgáz hőmérséklet (50/30˚C) (min/max) | ˚C | 31,4/45,6 | 31,4/47,9 | 30,7/45,4 | 31,2/46,1 | 29,7/47,6 | 31/44,9 | 31,6/48,3 |
| NOx osztály |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 |
| NOx kibocsátás | mg/kWh | 35,0 | 41,0 | 34,0 | 39,0 | 21,0 | 16,0 | 25,0 |
| Gáz fogyasztás (min/max) | m³/h | 4,9/25,5 | 4,8/30,0 | 6,9/35,2 | 8,8/44,6 | 10,8/53,5 | 8,5/64,5 | 12,1/69,8 |
| INSTALLÁCIÓS ADATOK |
| Előremenő víz (F) / visszatérő méret (E) | DN | 50/50 | 50/50 | 100/100 | 100/100 | 100/100 | 100/100 | 100/100 |
| Friss levegő (A) / füstgáz méret (G)(B23) | mm | 100/200 | 100/200 | 125/250 | 200/250 | 200/250 | 200/250 | 200/250 |
| Gáz csatlakozási méret (S) | DN | 32 | 32 | 50 | 65 | 65 | 65 | 65 |
| ELEKTROMOS ADATOK |
| Elektromos csatlakozás | V/Hz | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 |
| Electromos fogyasztás | W | 260 | 310 | 260 | 450 | 670 | 900 | 942 |
| ÁLTALÁNOS ADATOK |
| Energia hatékonysági osztály |  | A | A | A | A | A | A | A |
| Zajszint | dB(A) | 63,7 | 65,2 | 67,6 | 64,2 | 68,4 | 70,1 | 72,3 |
| Méretek (SzxMxM) | mm | 690x1460x1360 | 690x1460x1360 | 835x1220x1600 | 935x1420x1600 | 935x1705x1600 | 935x1705x1600 | 935x1745x1600 |
| Kazán súlya | kg | 280 | 280 | 305 | 381 | 425 | 452 | 525 |

Egyedülálló kazán

06

Alubox X-treme

*A szürke zónában ikerkazánok találhatóak.

Alubox X-treme

710

880

1065

1315

1460

1550

*1760	*2630	*2920	*3100

134,6/685,6

129,6/669,2

145,9/711,3

95,7/97,8

108,7/104,1

108,5

20:100

0,8/6

68.7

6,7/30,4

7,2

90

95

G20 20

220

63/314

9,0/9,1

60,0/70,0

31,3/43,0

6

23,0

14,0/71,8

100/100

200/250

65

230/50

880

A 71,9

132,9/849,4

124/824,5

142,3/885,1

96,8/97,7

107,5/104,6

108,7

16:100

0,8/6

99.7

6,2/38,1

6,0

90

95

G20 20

179

60/389

9,1/9,0

59,4/69,5

30,3/46,3

6

32,0

13,4/87,9

125/125

200/250

65

400/50

1466

A 73,7

159,5/1025

152,9/999,9

171,9/1065,5

96,9/97,7

108,2/104,9

108,4

16:100

0,8/6

117.7

7,3/45,9

6,3

90

95

G20 20

252

73/467

8,92/9,1

59,6/68,7

31,2/45,0

6

32

16,4/106,6

125/125

200/250

65

400/50

2213

A 75,5

220,0/1261,0

212,0/1220,0

235,0/1315,0

96,5/97,3

107,2/104,7

108,0

18:100

0,8/6

135,8

9,2/55,5

6,9

90

95

G20 20

265

104/556

8,6/9,4

59,6/68,7

46,7/31,1

6

40

22,7/129,6

125/125

200/250

65

400/50

3162

A 77,2

250,0/1400,0

243,0/1360,0

268,0/1460,0

97,1/97,4

107,4/104,6

108,1

18:100

0,8/6

153.8

10,3/61,1

7,1

90

95

G20 20

221

112/622

8,9/8,9

59,8/67,3

30,8/42,0

6

31

25,5/139,0

125/125

200/250

65

400/50

3726

A 76,4

250,0/1490,0

243,0/1454,0

268,0/1555,0

97,1/97,3

107,4/104,4

108,04

17:100

0,8/6

153.8

10,3/63,5

7,0

90

95

G20 20

255

112/668

9,07/9,11

59,8/67,5

30,8/43,1

6

37

25,5/149,4

125/125

200/250

65

400/50

4306

A 75,3

132,9/1698

124/1649

142,3/1770

96,8/97,7

107,5/104,6

108,7

8:100

0,8/6

2x99,7

6,2/38,1

5,9

90

95

G20 20

179x2

60/389

9,05/9

59,4/69,5

30,3/46,3

6

32

2x13,4/87,9

125/125

200/250

65

400/50

2932

A 78,6

220/2522

212/2440

235/2630

96,5/97,3

107,2/104,7

108

9:100

0,8/6

2x135,8

9,2/51,1

6,8

90

95

G20 20

265x2

104/556

8,6/9,4

59,6/68,7

46,7/31,1

6

40

2x22,7/129,6

125/125

200/250

65

400/50

6324

A 77,2

250/2800

243/2720

268/2920

97,1/97,4

107,4/104,6

108,1

9:100

0,8/6

2x153,8

10,3/61,1

7,1

90

95

G20 20

221x2

112/622

8,9/8,9

59,8/67,3

30,8/42,0

6

31

2x25,5/139,0

125/125

200/250

65

400/50

7452

A 76,4

250/2980

243/2908

268/3110

97,1/97,3

107,4/104,4

108

9:100

0,8/6

2x153,8

10,3/63,5

7,0

90

95

G20 20

255x2

112/668

9,1/9,1

59,8/67,5

30,8/43,1

6

37

25,5/149,4

125/125

200/250

65

400/50

8612

A 75,3

935x1705x1600

935x2140x1600

935x2140x1600

985x2730x1600

985x2730x1600

985x2730x1600

1738x2140x1600 1872x2680x1600 1872x2680x1600 1872x2680x1600

510

625

685

811

925

925

1120

1630

1700

1700

Iker kazánok

07

Alubox

Álló kondenzációs kazán

50-2200 kW teljesítmény tartomány Alacsony NOx kibocsátás

Alacsony füstgáz hőmérséklet

Aluminum fűtési hőcserélő

Hatásfok akár %108,2  EN 15502-1

+A1szerint

Modulációs ráta akár 14:100

Kaszkád vezérlés akár 16 kazánig Hermetikus és nem hermetikus füstgáz opciók Alacsony zajszint

Energia Osztály : A

6 bar üzemi nyomás

08

Alubox

Magas korrózióállósság

Legújabb technológia, alacsony kibocsátású előkeveréses égő Nagy modulációjú és energiahatékony ventilátor

Alacsony emissziós értékekkel,

ECO-barát GASSERO.

Biztonsági rendszerek:

Fagy védelem

Túlfűtés védelem

Alacsony nyomás és túlnyomás védelem

Füstgáz hőmérséklet és víznyomás védelem

Szivattyú/szelep védelem

Legionella védelem a HMV tartály számára

Kondenzátum elzáródás védelem szifon érzékelővel

Ventillátor sebesség védelem

Felületi hőmérséklet védelem

Nagynyomású kapcsoló gázvezetékhez

09

Alubox

Álló kondenzációs kazán

Műszaki specifikáció

Alubox

|  |  | 50 | 70 |  | 90 | 115 | 125 | 150 | 208 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TELJESÍTMÉNY ADATOK | Egység |  |  |  |  |  |  |  |  |  |
| Névleges hőterhelés (min/max) | kW |  | 7,6/49,2 | 10,2/65,6 |  | 14,9/88,3 | 14,9/112,3 | 19,9/123,5 | 19,9/143,1 | 35,3/200,0 |
| Névleges hőtljesítmény (80/60°C) (min/max) | kW |  | 7,3/47,8 | 9,9/63,4 |  | 14,3/86,3 | 14,3/109,5 | 19,2/120,8 | 19,2/139,8 | 34,5/195,2 |
| Névleges hőtljesítmény (50/30°C) (min/max) | kW |  | 8,4/51,4 | 11,6/68,5 |  | 15,1/91 | 15,1/118,1 | 22,3/128 | 22,3/149,1 | 36,68/207,9 |
| Fűtési hatásfok (80/60°C) (min/max) | % |  | 96,9/97,7 | 96,7/97,2 |  | 96,8/98,4 | 96,79/98,16 | 97,0/98,3 | 97,0/98,2 | 97,7/97,6 |
| Fűtési hatásfok (50/30°C) (min/max) | % |  | 108,1/105,9 | 108,0/103,9 |  | 108,2/105,0 | 108,19/104,79 | 108,1/104,4 | 108,1/103,2 | 103,2/104 |
| Hatásfok részterhelésnél (36/30°C) | % |  | 108,56 | 108,4 |  | 108,5 | 108,65 | 108,5 | 108,4 | 107,4 |
| Modulációs ráta |  |  | 16:100 | 16:100 |  | 17:100 | 14:100 | 17:100 | 14:100 | 18:100 |
| HIDRAULIKUS ADATOK |  |  |  |  |  |  |  |  |  |  |
| Üzemi víznyomás (min/max)) | bar |  | 0,8/6 | 0,8/6 |  | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 |
| Hőcserélő vízmennyisége | lt |  | 3,2 | 3,2 |  | 4,6 | 4,6 | 6 | 6 | 29,1 |
| Víz áramlási mennyisége (min/max) | m³/h |  | 0,4/2,2 | 0,5/3,0 |  | 0,7/3,8 | 0,65/4,79 | 1,0/5,4 | 1,0/6,2 | 1,6/8,8 |
| Pump head | mWC |  | 3,0 | 3,0 |  | 5,0 | 5,0 | 5,5 | 5,5 | 5,3 |
| Max. üzemi hőmérséklet | ˚C |  | 85 | 85 |  | 85 | 85 | 85 | 85 | 90 |
| Hőmérséklet korlátozása | ˚C |  | 95 | 95 |  | 95 | 95 | 95 | 95 | 105 |
| GÁZ ÉS ÉGÉSTERMÉK ADATOK |  |  |  |  |  |  |  |  |  |  |
| Gáz típusa |  |  | G20 | G20 |  | G20 | G20 | G20 | G20 | G20 |
| Gáz csatlakozási nyomás (G20/G31) | mbar |  | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 |
| Füstgáz nyomása | Pa |  | 100 | 130 |  | 170 | 200 | 220 | 330 | 160 |
| Égéstermékek áramlási sebessége (min/max) | g/sn |  | 0,8/5,1 | 1,1/6,8 |  | 1,5/9,1 | 1,5/11,7 | 2,1/12,8 | 2,1/14,9 | 16,5/89,3 |
| CO2 kibocsátás (min/max) | % |  | 9,3/9,4 | 9,1/9,6 |  | 9,4/9,3 | 9,4/9,4 | 9,5/9,5 | 9,5/9,6 | 8,8/9,3 |
| Füstgáz hőmérséklet (80/60˚C) (min/max) | ˚C |  | 54,7/65,6 | 55,4/72,1 |  | 56,8/61,4 | 56,8/64,9 | 56,9/61,8 | 56,9/70,3 | 53,2/63,4 |
| Füstgáz hőmérséklet (50/30˚C) (min/max) | ˚C |  | 29,5/45,1 | 30,1/52,3 |  | 30,2/448,8 | 30,2/53,5 | 30,5/44,9 | 30,5/47,1 | 29/52,7 |
| NOx osztály |  |  | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 |
| NOx kibocsátás | mg/kWh |  | 37 | 28 |  | 39 | 43 | 46 | 44 | 33,9 |
| Gáz fogyasztás (min/max) | m³/h |  | 0,8/5,1 | 1,1/6,9 |  | 1,5/9,1 | 1,5/11,8 | 2,2/12,8 | 2,2/15,1 | 3,7/21,2 |
| INSTALLÁCIÓS ADATOK |  |  |  |  |  |  |  |  |  |  |
| Előremenő víz (F) / visszatérő méret (E) | DN |  | 25/25 | 25/25 |  | 25/25 | 25/25 | 25/25 | 25/25 | 50/50 |
| Friss levegő (A) / füstgáz méret (G)(B23) | mm |  | 80/100 | 80/100 |  | 110/100 | 110/100 | 110/100 | 110/100 | 100/200 |
| Gáz csatlakozási méret (S) | DN |  | 25 | 25 |  | 25 | 25 | 25 | 25 | 32 |
| ELEKTROMOS ADATOK |  |  |  |  |  |  |  |  |  |  |
| Elektromos csatlakozás | V/Hz |  | 230/50 | 230/50 |  | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 |
| Elektromos fogyasztás | W |  | 52 | 97 |  | 116 | 203 | 212 | 313 | 450 |
| ÁLTALÁNOS ADATOK |  |  |  |  |  |  |  |  |  |  |
| Energia hatékonysági osztály |  |  | A | A |  | A | A | A | A | A |
| Zajszint | dB(A) |  | 57,2 | 66,2 |  | 58,8 | 61,3 | 66,4 | 69,3 | 62,1 |
| Méretek (SzxMxM) | mm |  | 640x575x1095 | 640x575x1095 |  | 640x575x1095 | 640x575x1095 | 640x575x1095 | 640x575x1095 | 645x1420x1420 |
| Kazán súlya | kg |  | 85 | 85 |  | 85 | 93 | 103 | 103 | 262 |

Iker kazán

10

Alubox

*A szürke zónában ikerkazánok találhatóak.

Alubox

290

540

700

1100

*2200

|  | 48/280,0 | 81,9/517,0 | 101,4/661,0 | 150,5/1026,8 | 301,0/2059,2 |
| --- | --- | --- | --- | --- | --- |
|  | 46,7/274,1 | 79,1/502,9 | 97,8/643,1 | 146/999,1 | 292/2003,6 |
|  | 51,4/286,2 | 84,7/539,2 | 107,8/708,4 | 160,7/999,1 | 321,4/2215,2 |
|  | 97,3/97,9 | 96,6/97,3 | 96,5/97,3 | 97,0/97,3 | 97,0/97,3 |
|  | 107,5/103,8 | 105,0/104,0 | 107/107,4 | 107,1/107 | 107,1/107 |
|  | 107,3 | 106,7 | 108,6 | 108 | 108 |
|  | 18:100 | 16:100 | 16:100 | 15:100 | 15:100 |
|  | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 |
|  | 40,6 | 75,5 | 99,2 | 155,1 | 2x155,1 |
|  | 2,3/12,2 | 3,4/23,6 | 4,7/31,0 | 7,0/42,3 | 7,0/93,8 |
|  | 6,5 | 5,2 | 5,2 | 5,4 | 5,4x2 |
|  | 90 | 90 | 90 | 90 | 90 |
|  | 105 | 95 | 95 | 95 | 95 |
|  | G20 | G20 | G20 | G20 | G20 |
|  | 20 | 20 | 20 | 20 | 20 |
|  | 160 | 150 | 150 | 150 | 2x150 |
|  | 22,5/119,6 | 38,0/235,1 | 47,0/292,4 | 69,1/459,6 | 69,1/459,6 |
|  | 8,8/9,8 | 8,9/9,1 | 8,9/9,4 | 9,0/9,3 | 9,0/9,3 |
|  | 54,2/64,6 | 55,5/63,6 | 61,4/65,8 | 61,9/64,6 | 61,9/64,6 |
|  | 29/47,4 | 30,3/40,1 | 34,2/34,5 | 29,4/33,8 | 29,4/33,8 |
|  | 6 | 6 | 6 | 6 | 6 |
|  | 62,6 | 38,0 | 53,0 | 48,0 | 48,0 |
|  | 5,18/29,6 | 8,5/54,0 | 10,5/68,6 | 15,8/97,0 | 15,8/217,9 |
|  | 50/50 | 80/80 | 80/80 | 100/100 | 100/100 |
|  | 100/200 | 125/250 | 125/250 | 200/250 | 200/250 |
|  | 32 | 65 | 65 | 65 | 65 |
|  | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 |
|  | 510 | 1400 | 1620 | 2650 | 5300 |
|  | A | A | A | A | A |
|  | 64,3 | 66,5 | 71,2 | 74,9 | 74,9 |
|  | 645x1420x1420 | 838x1731x1680 | 838x1731x1680 | 898x2079x1670 | 1738x2079x1670 |
|  | 295 | 450 | 510 | 680 | 1378 |

Alubox 70-115-150

Alubox 208-290

Alubox 540-700-1100

11

Ultrabox

Álló kondenzációs kazán

210-2660 kW teljesítmény tartomány Alacsony CO kibocsátás

Alacsony füstgáz hőmérséklet Rozsdamentes acél fűtési hőcserélő Hatásfok akár 108,1%  EN 15502-1+A1 szerint

Modulációs ráta 4:100

Kaszkád vezérlés akár 16 kazánig Alacsony NOx kibocsátás

Hermetikus és nem hermetikus füstgáz opciók

Alacsony zajszint

Energia Osztály: A

6 bar üzemi nyomás

12

Ultrabox

Magas korrózióállósság

Legújabb technológia, alacsony kibocsátású előkeveréses égő Nagy modulációjú és energiahatékony ventilátor

Fejlett kondenzációs technológia,

alacsony gázfogyasztás.

Biztonsági rendszerek:

Fagy védelem

Túlfűtés védelem

Alacsony nyomás és túlnyomás védelem

Füstgáz hőmérséklet és víznyomás védelem

Szivattyú/szelep védelem

Legionella védelem a HMV tartály számára

Kondenzátum elzáródás védelem szifon érzékelővel

Ventillátor sebesség védelem

Felületi hőmérséklet védelem

Nagynyomású kapcsoló gázvezetékhez

13

Ultrabox

Álló kondenzációs kazán

Műszaki specifikáció

| Ultrabox |
| --- |
|  |  |  | 210 |  | 255 |  | 315 |  | 430 |  | 500 |  | 530 660 |
| TELJESÍTMÉNY ADATOK | Egység |  |  |  |  |  |  |  |  |  |  |  |
| Névleges hőterhelés (min/max) | kW |  | 30,3/198,3 |  | 35,0/237,7 |  | 35,1/295,3 |  | 41,8/405,5 |  | 60,0/470,0 |  | 60,0/500,0 60,0/620,0 |
| Névleges hőtljesítmény (80/60°C) (min/ma | x) kW |  | 29,5/194,2 |  | 34,1/232,5 |  | 34,2/289,5 |  | 40,6/393,7 |  | 58,4/456,4 |  | 58,4/486,4 58,4/602,6 |
| Névleges hőtljesítmény (50/30°C) (min/max) | kW | 32,6/212,1 | 37,7/256,5 | 37,7/317,8 | 45,0/430,3 | 64,8/503,4 | 64,8/536,0 | 63,4/665,0 |
| Fűtési hatásfok (80/60°C) (min/max) | % | 97,5/97,9 | 97,5/97,8 | 97,5/98,0 | 97,3/97,1 | 97,4/97,1 | 97,4/97,3 | 97,4/97,2 |
| Fűtési hatásfok (50/30°C) (min/max) | % | 107,2/107,0 | 107,3/107,0 | 107,5/107,0 | 107,9/106,1 | 108,1/107,1 | 108,1/107,2 | 108,1/107,4 |
| Hatásfok részterhelésnél (36/30°C) | % | 108,4 | 108,4 | 108,4 | 108,3 | 108,0 | 108,5 | 108,5 |
| Modulációs ráta |  | 16:100 | 15:100 | 12:100 | 11:100 | 13:100 | 12:100 | 10:100 |
| HIDRAULIKUS ADATOK |  |  |  |  |  |  |  |  |
| Üzemi víznyomás (min/max) | bar | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 |
| Hőcserélő vízmennyisége | lt | 29,4 | 29,4 | 29,4 | 58,8 | 71,4 | 71,4 | 71,4 |
| Víz áramlási mennyisége (min/max) | m³/h | 1,4/9,2 | 1,7/11,2 | 1,6/13,8 | 1,83/18,3 | 2,7/21,7 | 2,7/22,8 | 2,3/28,9 |
| Pump head | mWC | 6,4 | 6,7 | 6,7 | 6,4 | 6,7 | 6,7 | 6,7 |
| Max. üzemi hőmérséklet | ˚C | 90 | 90 | 90 | 90 | 90 | 90 | 90 |
| Hőmérséklet korlátozása | ˚C | 95 | 95 | 95 | 95 | 95 | 95 | 95 |
| GÁZ ÉS ÉGÉSTERMÉK ADATOK |  |  |  |  |  |  |  |  |
| Gáz típusa |  | G20 | G20 | G20 | G20 | G20 | G20 | G20 |
| Gáz csatlakozási nyomás (G20/G31) | mbar | 20 | 20 | 20 | 20 | 20 | 20 | 20 |
| Füstgáz nyomása | Pa | 160 | 160 | 160 | 160 | 160 | 160 | 160 |
| Égéstermékek áramlási sebessége (min/max) g/sn 13/88 15/107 15/129 13/176 15/214 15/236 15/258 |
| CO2 kibocsátás (min/max) | % | 9,6/9,4 | 9,4/9,2 | 9,7/9,4 | 9,6/9,4 | 9,4/9,2 | 9,6/9,3 | 9,7/9,4 |
| Füstgáz hőmérséklet (80/60˚C) (min/max) | ˚C | 60,3/62,1 | 60,3/64,8 | 63,4/74,3 | 60,3/62,1 | 60,3/64,8 | 61,5/67,3 | 61,5/73,1 |
| Füstgáz hőmérséklet (50/30˚C) (min/max) | ˚C | 32,1/36,1 | 32,1/35,5 | 38,5/46,6 | 32,1/36,1 | 32,1/35,5 | 33,0/41,5 | 32,9/47,7 |
| NOx osztály |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 |
| NOx kibocsátás | mg/kWh | 35 | 37 | 39 | 35 | 39 | 39 | 39 |
| Gáz fogyasztás (min/max) | m³/h | 3,1/20,5 | 3,6/24,8 | 3,6/30,7 | 4,1/38,2 | 5,5/45,0 | 5,54/47,7 | 5,54/59,1 |
| INSTALLÁCIÓS ADATOK |  |  |  |  |  |  |  |  |
| Előremenő víz (F) / visszatérő méret (E) | DN | 65/65 | 65/65 | 65/65 | 65/65 | 65/65 | 65/65 | 65/65 |
| Friss levegő (A) / füstgáz méret (G)(B23) | mm | 100/170 | 100/170 | 100/170 | 200/200 | 200/200 | 200/200 | 200/200 |
| Gáz csatlakozási méret (S) | DN | 32 | 32 | 65 | 65 | 65 | 65 | 65 |
| ELEKTROMOS ADATOK |  |  |  |  |  |  |  |  |
| Elektromos csatlakozás | V/Hz | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 | 230/50 |
| Elektromos fogyasztás | W | 360 | 410 | 470 | 720 | 830 | 880 | 940 |
| ÁLTALÁNOS ADATOK |  |  |  |  |  |  |  |  |
| Energia hatékonysági osztály |  | A | A | A | A | A | A | A |
| Zajszint | dB(A) | 72,6 | 74,1 | 75,7 | 76,1 | 77,4 | 77,4 | 78,0 |
| Méretek (SzxMxM) mm 691x995x1750 691x995x1750 691x995x1750 960x1520x1072 960x1846x1072 960x1846x1072 960x1846x1072 |
| Kazán súlya |  | kg |  | 260 |  | 260 |  | 270 |  | 451 |  | 451 |  | 461 | 471 |

A

A

F

E

F

E

S

S

G

G

J

J

F

Iker kazán

E S

G

14

Ultrabox

G

J

G

J

Ultrabox 1030-1330

|  |  |  | Ultrabox |  |
| --- | --- | --- | --- | --- |
|  | *860 | 1030 | *1060 | *1320 | 1330 | *2060 | *2660 |
|  | 41,8/811,0 | 95,0/956,0 | 60,0/1000,0 | 60,0/1240 | 95,0/1235,0 | 95,0/1912,0 | 95,0/2470,0 |
|  | 40,6/787,4 | 92,2/932,2 | 58,4/972,8 | 58,4/1205,2 | 92,2/1205,6 | 92,2/1864,4 | 92,2/2411,2 |
|  | 45,0/860,6 | 102,0/1030,3 | 64,8/1072,0 | 63,4/1330,0 | 102,0/1335,0 | 102,0/2060,6 | 102,0/2670,0 |
|  | 97,3/97,1 | 97,1/97,5 | 97,4/97,3 | 97,4/97,2 | 97,1/97,6 | 97,1/97,5 | 97,1/97,6 |
|  | 107,9/106,1 | 108,0/107,8 | 108,1/107,2 | 108,1/107,4 | 107,3/108,1 | 108,0/107,8 | 107,3/108,1 |
|  | 108,3 | 108,1 | 108,5 | 108,5 | 108,3 | 108,1 | 108,3 |
|  | 11:100 | 10:100 | 6:100 | 5:100 | 8:100 | 5:100 | 4:100 |
|  | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 | 0,8/6 |
|  | 2x58,8 | 140,0 | 2x71,4 | 2x71,4 | 140,0 | 2x140,0 | 2x140,0 |
|  | 1,83/18,3 | 4,4/44,1 | 2,7/22,8 | 2,3/28,9 | 4,4/56,1 | 4,4/44,1 | 4,4/56,1 |
|  | 6,4 | 6,7 | 6,7 | 6,7 | 6,7 | 6,7 | 6,7 |
|  | 90 | 90 | 90 | 90 | 90 | 90 | 90 |
|  | 95 | 95 | 95 | 95 | 95 | 95 | 95 |
|  | G20 | G20 | G20 | G20 | G20 | G20 | G20 |
|  | 20 | 20 | 20 | 20 | 20 | 20 | 20 |
|  | 160 | 100 | 160 | 160 | 265 | 100 | 265 |
|  | 13/176 | 87/440 | 15/236 | 15/258 | 104/556 | 87/440 | 104/556 |
|  | 9,6/9,4 | 9,1/9,4 | 9,6/9,3 | 9,7/9,4 | 9,1/9,4 | 9,1/9,4 | 9,1/9,4 |
|  | 60,3/62,1 | 65,1/63,8 | 61,5/67,3 | 61,5/73,1 | 65,1/66,1 | 65,1/63,8 | 65,1/66,1 |
|  | 32,1/36,1 | 37,4/35,4 | 33,0/41,5 | 32,9/47,7 | 37,4/36,3 | 37,4/35,4 | 37,4/36,3 |
|  | 6 | 6 | 6 | 6 | 6 | 6 | 6 |
|  | 35 | 41 | 39 | 39 | 40 | 41 | 40 |
|  | 4,1/76,4 | 8,8/87,0 | 5,54/47,7 | 5,54/118,2 | 8,9/116,9 | 8,8/174 | 8,9/233,8 |
|  | 65/65 | 100/100 | 65/65 | 65/65 | 100/100 | 100/100 | 100/100 |
|  | 200/200 | 200/300 | 200/200 | 200/200 | 200/300 | 200/300 | 200/300 |
|  | 65 | 65 | 65 | 65 | 65 | 65 | 65 |
|  | 230/50 | 400/50 | 230/50 | 230/50 | 400/50 | 400/50 | 400/50 |
|  | 1440 | 2400 | 880 | 1880 | 3200 | 4800 | 6400 |
|  | A | A | A | A | A | A | A |
|  | 76,1 | 82,4 | 77,4 | 78,0 | 84,3 | 82,4 | 84,3 |
|  | 1975x1625x1502 | 1184x2080x1385 | 1835x1846x1270 | 1835x1846x1270 | 1184x2490x1385 | 2340x2220x1635 | 2235x2492x1588 |
|  | 942 | 897 | 962 | 982 | 925 | 1834 | 1890 |

*A szürke zónában ikerkazánok találhatóak.	 	Ultrabox 530-660

Ultrabox 1000-1125

15

Superbox

Álló kondenzációs kazán

150-1060 kW teljesítmény tartomány Alacsony NOx kibocsátás

Alacsony füstgáz hőmérséklet Rozsdamentes acél fűtési hőcserélő Akár 109%-os hatásfok EN 15502-1+A1 szerint

Akár 3:100-as modulációs ráta Kaszkád vezérlés akár 16 kazánig

Hermetikus és nem hermetikus füstgáz opciók

Alacsony zajszint

Energia Osztály: A

6 bar üzemi nyomás

Magas korrózióállósság

Legújabb technológia, alacsony kibocsátású előkeveréses égő Nagy modulációjú és energiahatékony ventilátor

Biztonsági rendszerek:

Fagy védelem

Túlfűtés védelem

Alacsony nyomás és túlnyomás védelem

Füstgáz hőmérséklet és víznyomás védelem

Szivattyú/szelep védelem

Legionella védelem a HMV tartály számára

Kondenzátum elzáródás védelem szifon érzékelővel

Ventillátor sebesség védelem

Felületi hőmérséklet védelem

Nagynyomású kapcsoló gázvezetékhez

16

Superbox

* A szürke zónában ikerkazánok találhatóak.

Műszaki specifikáció

TELJESÍTMÉNY ADATOK

Egység

Superbox

150	500

*1000

Szimpla kazán

Névleges hőterhelés (min/max)

Névleges hőtljesítmény (80/60°C) (min/max) Névleges hőtljesítmény (50/30°C) (min/max) Fűtési hatásfok (80/60°C) (min/max)

Fűtési hatásfok (50/30°C) (min/max) Hatásfok részterhelésnél (36/30°C) Modulációs ráta

HIDRAULIKUS ADATOK

Üzemi víznyomás (min/max) Hőcserélő vízmennyisége

Víz áramlási mennyisége (min/max) Pump head

Max. üzemi hőmérséklet Hőmérséklet korlátozása

GÁZ ÉS ÉGÉSTERMÉK ADATOK

Gáz típusa

Gáz csatlakozási nyomás (G20/G31)

Füstgáz nyomása

kW kW kW

%

%

%

bar lt

m³/h mWC

˚C

˚C

mbar Pa

21,5/152

20,9/146

23,4/158,8

97,2/96,1

109/104,5

109,1

15:100

0,8/6

11,4

1,0/6,7

8,6

90

105

G20 20

310

27,2/498,5

26,3/481,7

29,1/527,4

96,5/96,6

106,5/105,5

107,0

6:100

0,8/6

69,8

1,2/21,4

7,2

90

105

G20 20

100

27,2/996,9

26,3/962,1

29,1/1051,9

96,5/96,5

106,6/105,3

106,9

3:100

0,8/6

139,6

1,2/42,8

7,2

90

105

G20 20

100

Égéstermékek áramlási sebessége (min/max) g/sn

9,7/67,3

12,6/226,7

12,6/449,1

CO2 kibocsátás (min/max)

Füstgáz hőmérséklet (80/60˚C) (min/max) Füstgáz hőmérséklet (50/30˚C) (min/max) NOx osztály

NOx kibocsátás

Gáz fogyasztás (min/max)

INSTALLÁCIÓS ADATOK

Előremenő víz (F) / visszatérő méret (E) Friss levegő (A) / füstgáz méret (G)(B23) Gáz csatlakozási méret (S) ELEKTROMOS ADATOK

Elektromos csatlakozás Elektromos fogyasztás ÁLTALÁNOS ADATOK

Energia hatékonysági osztály Zajszint

Méretek (SzxMxM) Kazán súlya

%

˚C

˚C

mg/kWh m³/h

DN

mm DN

V/Hz W

dB(A)

mm kg

9,4/9,8

59,4/82,5

32,4/62,6

6

41

2,3/15,6

32/32

110/100

25

230/50

460

A 61,7

555x780x990

110

9/9,2

59,8/80,3

30,6/43,2

6

50

2,8/51,8

65/65

100/180

50

230/50

900

A 68,3

715x1610x1394

522

9/9,2

59,7/80,5

30,6/43,9

6

59

2,8/103,6

65/65

100/180

65

400/50

1440

A 72,1

1340x1620x1390

640

Iker kazán

17

Optionális kiegészítők

Termék kép

Termék név

Specifikáció

|  | Külső érzékelő | -50 ° C és 70 ° C között működik. Max. távolság 120 m 1,5 mm² kábellel. Tűrés ± 1 K |
| --- | --- | --- |
|  | Hőmérséklet érzékelő | -30 ° C és 125 ° C között működik. Max. távolság 120 m 1,5 mm² kábellel. Tűrés ± 0,5 K |
|  | Merülő hőmérséklet érzékelő | 0 ° C és 95 ° C között működik. Tűrés ± 0,5 K. |
|  | Külső zóna modul | Biztosítja a hőmérséklet alapú zónák háromutas szelepvezérlését. További relét és érzékelő csatlakoztatást igényel. |
|  | Helyiség termosztát | Biztosítja a helyiség hőmérsékletének beállítását és az üzemmód kiválasztását. |
|  | Modbus Module | Biztosítja a kapcsolatot az épületirányítási rendszerekkel (BMS). |

18

19

Füstgáz alkalmazások

IRIS Levegő szabályozó

Levegőbeállítási lehetőséget biztosít radiális légcsatornákban.

A kézi vezérlésű lengéscsillapító beállítható a szükséges légmennyiséghez, és rögzíthető rajta lévő reteszelő mechanizmussal.

Horganyzott acéllemezből készül.

Ideális légáram-beállító és mérőberendezés radiális légcsatornákhoz.

Egységes belső levegőáramot biztosít, állítható íriszátmérővel.

Alkalmas folyamatos használatra -10 ° C és +80 ° C között.

Installációs sémák

HMV + Radiátor (Hidraulikus váltó)

DHW Circuit Pump Control 2x1,5 mm²

Radiator Circuit Pump Control 2x1,5 mm²

Boiler 2.../...64	Boiler 1

Primary Pump Control	Primary Pump Control 2x1,5 mm²	2x1,5 mm²

DHW Circuit Pump Supply 3x1,5 mm²

Radiator Circuit Pump Supply 3x1,5 mm²

ELECTRICAL

PANEL

Boiler Supply

For Monophase (230V) Boiler 3x1,5mm² For Three-phase (400V) Boilers 5x2,5mm²

Boiler 1

Primary Pump Supply 3x1,5 mm²

Boiler 2.../...64 Primary Pump Supply 3x1,5 mm²

DHW CIRCUIT

RADIATOR CIRCUIT

2x1,5 mm² DHW Sensor

2x1,5 mm² Cascade Sensor

2x1,5 mm² Outdoor Sensor (Max 50 m)

F

S

E

F	S

E

2x1,5 mm² Cascade Cable

T   M

WATER SOFTENER UNIT

1

... 2 / 3 / 4 ...

(max. 16)

16

220V

HMV + Radiátor (Hidrauliku váltó and 3-járatú szelep)

DHW Circuit Pump Control 2x1,5 mm²

Radiator Circuit Pump Control 2x1,5 mm²

Boiler 2.../...64	Boiler 1

Primary Pump Control	Primary Pump Control 2x1,5 mm²	2x1,5 mm²

DHW Circuit Pump Supply 3x1,5 mm²

Radiator Circuit Pump Supply 3x1,5 mm²

ELECTRICAL

PANEL

Boiler Supply

For Monophase (230V) Boiler 3x1,5mm² For Three-phase (400V) Boilers 5x2,5mm²

Boiler 1

Primary Pump Supply 3x1,5 mm²

Boiler 2.../...64 Primary Pump Supply 3x1,5 mm²

DHW CIRCUIT

RADIATOR CIRCUIT

2x1,5 mm² DHW Sensor

2x1,5 mm² Sensor Cable

2x1,5 mm² Cascade Sensor

3x1,5 mm² 3 Way Valve Supply

2x1,5 mm² Outdoor Sensor (Max 50 m)

F

S

E

F

S

E

2x1,5 mm² Cascade Cable

M

HYDRAULICSEPARATOR

T  M

WATER SOFTENER UNIT

1

... 2 / 3 / 4 ...

(max. 16)

16

220V

T

M

PUMP

VALVE	NON-RETURN VALVE         STRAINER

TEMPERATURE SENSOR

OUTDOOR SENSOR    AIR RELIEF VALVE       THERMOMETER           MANOMETER	SAFETY VALVE

DRAIN

AIR SEPERATOR      DIRT SEPERATOR    EXPANSION VESSEL

20

Installációs sémák

DHHMV+ PAdló fűtés (Lemezes hőcserélő és 3-járatú szelep)

ELECTRICAL PANEL

DHW Circuit Pump Control 2x1,5 mm²

Floor Heating Circuit	Boiler 2.../...64	Boiler 1

Pump Control	Primary Pump Control	Primary Pump Control

2x1,5 mm²	2x1,5 mm²	2x1,5 mm²

DHW Circuit Pump Supply 3x1,5 mm²

Floor Heating Pump Supply 3x1,5 mm²

Boiler Supply

For Monophase (230V) Boiler 3x1,5mm² For Three-phase (400V) Boilers 5x2,5mm²

Boiler 1

Primary Pump Supply 3x1,5 mm²

Boiler 2.../...64 Primary Pump Supply 3x1,5 mm²

2x1,5 mm² DHW Sensor

2x1,5 mm² Sensor Cable

2x1,5 mm² Cascade Sensor

3x1,5 mm² 3 Way Valve Supply

2x1,5 mm² Outdoor Sensor (Max 50 m)

F

S

E

F

S

E

2x1,5 mm² Cascade Cable

M

PLATE HEAT EXCHANGER

T  M

T  M

WATER SOFTENER UNIT

1

... 2 / 3 / 4 ...

(max. 16)

16

220V

HMV + Pdló fűtés (Hidraulikus váltó, Lemezes hőcserélő és 3-járatú szelep)

DHW Circuit Pump Control 2x1,5 mm²

Floor Heating Circuit	Boiler 2.../...64	Boiler 1

Pump Control	Primary Pump Control	Primary Pump Control

2x1,5 mm²	2x1,5 mm²	2x1,5 mm²

DHW Circuit Pump Supply 3x1,5 mm²

Floor Heating Pump Supply 3x1,5 mm²

ELECTRICAL

PANEL

Boiler Supply

For Monophase (230V) Boiler 3x1,5mm² For Three-phase (400V) Boilers 5x2,5mm²

FLOOR HEATING CIRCUIT

Boiler 1

Primary Pump Supply 3x1,5 mm²

Boiler 2.../...64 Primary Pump Supply 3x1,5 mm²

DHW CIRCUIT

2x1,5 mm² DHW Sensor

M

2x1,5 mm² Cascade Sensor

PLATE HEAT EXCHANGER

2x1,5 mm² Outdoor Sensor (Max 50 m)

F

S

E

F

S

E

2x1,5 mm² Cascade Cable

HYDRAULICSEPARATOR

T   M

WATER SOFTENER UNIT

1

... 2 / 3 / 4 ...

(max. 16)

16

220V

T

M

PUMP

VALVE	NON-RETURN VALVE         STRAINER

TEMPERATURE SENSOR

OUTDOOR SENSOR    AIR RELIEF VALVE       THERMOMETER           MANOMETER	SAFETY VALVE

DRAIN

AIR SEPERATOR      DIRT SEPERATOR    EXPANSION VESSEL

21

Installációs sémák

HMV + Magas hőmérsékletű kör + Radiátor (Hidraulikus váltó és 3-járatú szelep)

ELECTRICAL PANEL

DHW Circuit Pump Control 2x1,5 mm²

High Temperature	Radiator Circuit

Pump Control	Pump Control

2x1,5 mm²	2x1,5 mm²

Boiler 2.../...64	Boiler 1

Primary Pump Control	Primary Pump Control 2x1,5 mm²	2x1,5 mm²

Radiator Circuit Pump Supply 3x1,5 mm²

High Temperature Pump Supply 3x1,5 mm²

DHW Circuit Pump Supply 3x1,5 mm²

Boiler Supply

For Monophase (230V) Boiler 3x1,5mm² For Three-phase (400V) Boilers 5x2,5mm²

Boiler 1

Primary Pump Supply 3x1,5 mm²

Boiler 2.../...64 Primary Pump Supply 3x1,5 mm²

DHW CIRCUIT

RADIATOR CIRCUIT

HIGH TEMPERATURE

CIRCUIT

2x1,5 mm² DHW Sensor

2x1,5 mm² Cascade Sensor

2x1,5 mm² Outdoor Sensor (Max 50 m)

F

S

E

F	S

E

2x1,5 mm² Cascade Cable

HYDRAULICSEPARATOR

T  M

WATER SOFTENER

UNIT

1

... 2 / 3 / 4 ...

(max. 16)

16

220V

HMV + Magas hőmérsékletű kör + Radiátor (Lemezes hőcserélő és 3-járatú szelep)

DHW Circuit Pump Control 2x1,5 mm²

High Temperature Pump Control 2x1,5 mm²

Radiator Circuit	Boiler 2.../...64

Pump Control	Primary Pump Control

2x1,5 mm²	2x1,5 mm²

Boiler 1

Primary Pump Control 2x1,5 mm²

Radiator Circuit Pump Supply 3x1,5 mm²

High Temperature Pump Supply 3x1,5 mm²

DHW Circuit Pump Supply 3x1,5 mm²

ELECTRICAL

PANEL

Boiler Supply

For Monophase (230V) Boiler 3x1,5mm² For Three-phase (400V) Boilers 5x2,5mm²

Boiler 1

Primary Pump Supply 3x1,5 mm²

Boiler 2.../...64 Primary Pump Supply 3x1,5 mm²

DHW CIRCUIT

2x1,5 mm² Sensor Cable

RADIATOR CIRCUIT

HIGH TEMPERATURE

CIRCUIT

2x1,5 mm² DHW Sensor

3x1,5 mm² 3 Way Valve Supply

2x1,5 mm² Cascade Sensor

2x1,5 mm² Outdoor Sensor (Max 50 m)

F

S

E

F

S

E

2x1,5 mm² Cascade Cable

M

PLATE HEAT EXCHANGER

T  M

T  M

WATER SOFTENER

UNIT

1

... 2 / 3 / 4 ...

(max. 16)

16

220V

T

M

PUMP

VALVE	NON-RETURN VALVE         STRAINER

TEMPERATURE SENSOR

OUTDOOR SENSOR    AIR RELIEF VALVE       THERMOMETER           MANOMETER	SAFETY VALVE

DRAIN

AIR SEPERATOR      DIRT SEPERATOR    EXPANSION VESSEL

22

BOILER ROOM APPLICATION RECOMMENDATIONS

Gassero is strictly advising to use water softening unit before commissioning process for long term usage. Otherwise, system could harm because of undesirable substances.

It is highly recommended to use plate heat exchanger, if there is floor heating system on the heating line. The devices that are commissioned outside of the required conditions, could be out of warranty.

Water Condition Range

Total Hardness

°d

pH (Aluminium)

pH (Stainless)

Iron

(Not Diluted)	Condunctivity	Flushing

1	6,5-8,5	7,5-9,5	<10ppm	≤2000µS/cm	It is mandatory to comply with BSRIA

7593 (See: Gassero Flushing Process)

Nitrite protection should not be used in boilers with aluminum heat exchangers

WATER CONDITIONS

As GASSERO, we recommend flushing in the system to prolong the life of system and boilers. No acid-based products should be used during flushing.

The water used in the installation have to be city-water. Never use well-water

The boiler have to be serviced annually. All this maintenance should be made by authorized service, water values and the water softening unit (resin, salt etc.) values should be measured and maintained by service

Depending on the water conditions specified in the table, the problems that may occur in the boiler heat exchanger could make out of warranty.

Assembly and installation should made according to Gassero sample schemes.

Boiler (primary) pump have to be selected to in accordence with the required pressure and flow rate.

The boiler (primary) pump have to be in the direction of the installation return line to the boiler.

The system operating pressure should match with the working pressure of boiler. Sales Engineers could give consultancy.

All heat exchanger manufacturers; recommends to use of plate exchanger instead of the hydraulic separator for seperate the primary circuit and the secondary circuit.

HYDRAULIC

Domestic waste system could be used for condensate water. In system with a total power of 200 KW and above, a neutralization tank must be used. Boiler output and input diameters have to be strictly followed, other equipment should be selected according to the this diameters. In order to install other equipment, the diameter of the boiler out should not be reduced.

It is mandatory to use a suitable diameter filter and check valve to the boiler return line pipe at each boiler turn.

Please contact our service department about detail of collector connection in installation of floor type boiler.

Additional zone control modules and sensors have to be requested if there are equipment such as three-way valves and boilers that must be checked on the heating collector. Please contact our Sales Engineer for more information.

Have to be used air separator and dirt separator with hydraulic separator.

In case the plate heat exchanger is used instead of the hydraulic separator as the system separator, expansion tank have to be placed in the primary circuit. If an automatic filling valve is used in the system, a water meter have to be used for following how much water is added to the system.

In cascade systems, the sensor housing must be placed on the hydraulic separator or on the secondary flow line. If the system is separated by a plate heat exchanger, place the sensor housing on the secondary circuit flow line.

| ELECTRIC AND FLUE |  | 6A fuses have to be used for the power supply of the boilers. The electrical system must be grounded. |
| --- | --- | --- |
|  |  | Chimney connections have to be made in accordance with the chimney types and regulations. |
|  |  | The flue gas analysis measuring probe (probe hole) have to be opened by the flue company for each boiler. |
|  |  | Boiler chimneys should be extended by a minimum 1 meter from the boiler flue outlet direction and then connected to the chimney collector without elbows or with elbows. |
|  |  | If the chimney connections passes over the boiler, the connections should be checked properly and water tightening should be provided. Water in the chimney due to leaks may cause the system out of warranty. Adequate ventilation should be provided for the boiler room. |

| GAS AND OTHER |  | The operating pressure of the boilers in the natural gas installation is 21 Mbar. Therefore, it is necessary to use a regulator in the gas line. There should be a minimum distance of 1-2 meters between the regulator and the boiler gas flange. There should be discharge line after regulator for discharge of the excess air. |
| --- | --- | --- |
|  |  | In order to control the gas pressures, the manometer must be fitted before and after the regulator. |
|  |  | Gassero boilers are manufactured for heating and domestic water. Not suitable for commercial or industrial purposes. GASSERO shall not be held responsible for any problems arising out of the design purpose. |

23

www.gassero.com

Gassero Isı Teknolojileri 6DQ /WG

İstanbul Endüstri ve Ticaret Serbest Bölgesi (Free Zone)

4.Sokak No:8  34957 Tuzla / İstanbul

T: +90 (216) 394 09 85	Rev. 00 / 18.11.2019